[image: image1.jpg]


                                                                                                                                  Thermal Barrier


                                                                                                       Tentative Data 03


FOAM SAFE 

PRODUCT DESCRIPTION

FOAM SAFE is a cementitous thermal barrier coating for plastic foam insulations. It is factory precision mixed in 18 kg (40 lb) bags to which potable water is added. FOAM SAFE is I.C.B.O. approved. Recommendation  No. 4022, and is Underwriter’s Laboratories Listed Report 11944.

RECOMMENDED USES
FOAM SAFE thermal barrier can be used in any application wherein it is desirable to provide a protective thermal barrier over exposed plastic foam insulation as required by the Uniform Building Code. Typical constructions which would require this material would include:

· Controlled atmosphere fruit storage warehouses

· Fruit and vegetable cold storage warehouses

· Potato storage warehouses

· Freezers

· Breweries

· Restaurants

· Sports arenas

· Swimming pools

· Water treatment plants

· Fire stations

· Seed storage and processing

· Fish processing plants

· Aircraft hangars

· Furniture manufacturing

· Roof decks

· One coat stucco and/or plaster

· Interior finish for boats and ships-over plastic foam insulation

MIXING INSTRUCTIONS

Clean equipment is absolutely essential for mixing, pumping, and spraying FOAM SAFE.

1. Weigh or measure approximately 19-26 L (5-7 gal.) of potable water per 18 kg (40 lbs) bag of FOAM SAFE and place in mixer. If four (4 ) bags are used in one batch, approximately 83L (22 gal) of water should be placed in mixer.  Actual amount of water required may vary with hardness of water used, and length of hose through which material is to be pumped. Recommended amounts of water are based on soft water found in Western Washington, and on 15 m (50’) of hose length.

2. Add dry FOAM SAFE mix directly from bag to mixer. Mix 2 to 3 minutes. 

NOTE: Do not over-mix as this will increase the density and decrease the yield when  sprayed.

3. Proceed to spray immediately. The yield should be 3.7-4.6 m2 (40-50 sq. ft.) per bag, or 18.6 m2 (200 + sq. ft.) per four (4) bag batch, 13 mm (1/2”) thick.

CAUTION:
Do not let FOAM SAFE material become hard on or in equipment as it is very difficult to remove once it has set.

Do not apply FOAM SAFE when temperature is below 4.4(C (40(F).

After FOAM SAFE has been sprayed and taken the first set, it can be brushed, trowelled, floated, rolled or texturized in a wide variety of finishes. To seal the surface or achieve a desired color, use Masonry paint. It can be brushed or sprayed to FOAM SAFE thermal barrier coating after curing.



TYPICAL PHYSICAL PROPERTIES:



PROPERTY
TEST METHOD


VALUES

Dry Density
Underwriter’s Laboratories, Inc.

416 kg/m3 (26 Lbs. Per Cu. Ft.)

Wet Density
Underwriter’s Laboratories, Inc.

929 kg/m3 (58 Lbs. Per Cu. Ft.)

Dry Wgt.-13mm (1/2”) Thick
Underwriter’s Laboratories, Inc.

4.34 kg/m3 (.89 Lbs. Per Sq. Ft.)

Tensile Strength
Northwest Laboratories:
            2880 kg/m3(590 Lbs. Per Sq. Ft.)

  -Applied to plastic foam
Seattle, Washington




            


Indention Strength
Northwest Laboratories:

745 kPa (108 Lbs. Per Sq. In.)

  -Applied to plastic foam
Seattle, Washington

75 921kg/m3(15500 Lbs/Sq. Ft.)




           To indent coating 1.6 mm (1/16”)

Shear Strength
Northwest Laboratories:

13 148 kg/m3 (2693 Lbs./Sq.Ft.)

  -Applied to plastic foam
Seattle, Washington







Freeze/Thaw
Pacific Testing Laboratories:

After 20 cycles, no change.

  -Applied to plastic foam
Seattle, Washington






“K” Factor
Dynatech


“K”=.061 {W/ (mK)} (.425)

FOAM SAFE coating only


            “R”=2.35 Per In./ FOAM SAFE

Burning Characteristics:
ASTM E-84 Tunnel Furnace

Flamespread             0

FOAM SAFE coating only-
Test Method


Fuel Contributed      0

Applied to cement asbestos board   
Hardwood Plywood Mfrs. Ass.
Smoke Developed    0


Reston, Virginia







Surface Burning Characteristics
ASTM E-84 Tunnel Furnace

Flamespread
       0

FOAM SAFE Coating only
Test Method


Fuel Contributed      0

13mm  (1/2”) thick applied to
   Underwriter’s Laboratories, Inc.
Smoke Developed 0

cement asbestos board


North Brook, Illinois





Burning Characteristics

Underwriter’s Laboratories, Inc.

FOAM SAFE U.L. listed as a

FOAM SAFE coating applied
Enclosed Room Corner Fire Test
cementitous mixture for walls/

13mm (1/2”) thick over 101mm
      U.L Subject 1715


ceiling construction with regard 

(4”) plastic foam insulation (both




to flame propagation and 

polyurethane and polystyrene foam




damageability under specified 

were tested)







room fire conditions only.










Report R11944




Burning Characteristics

  I.C.B.O. Enclosed Room Corner
Findings: That FOAM SAFE 

FOAM SAFE coating applied
  Test: SW Research Institute

complies as a thermal barrier

To 101mm (4”) plastic foam
  San Antonio, Texas


under Section 1712 (C) of the 










1998 Uniform building code, 










subject to the conclusions in










I.C.B.O. Report No. 4022.




 

Disclaimer:  All guarantees and warranties as to products supplied by UCSC shall have only those guarantees and warranties expressed by the manufacturer.  Buyer's sole remedy as to any material claims will be against the manufacturer of the product.

The aforementioned data on this product is to be used as a guide and is subject to change without notice.  The information herein is believed to be reliable, but unknown risks may be present.  No warranties, expressed or implied, including patent warranties or warranties of merchantability or fitness for use, are made by UCSC or the manufacturer with respect to products or information set forth herein.  Nothing contained herein shall constitute a permission or recommendation to practice any invention covered by a patent without a license from the owner of the patent.  Accordingly, buyer assumes all risks whatsoever as to the use of these materials and buyer's exclusive remedy as to any breach of warranty, negligence or other claim shall be limited to the purchase price of the materials.  Failure to adhere to any recommended procedures shall relieve UCSC and the manufacturer of all liability with respect to the materials and the use thereof.

CHEMTREC EMERGENCY #:  1-800-424-9300

Corporate Office:

3010 W. Lincoln St.

Phoenix, AZ 85009

888-289-8272

602-269-9711

602-269-9115 fax 

www.ucscurethane.com
Regional Locations:

Las Cruces, NM

Denver, CO

Grand Prairie, TX

Atlanta, GA

Juarez, Mexico

